## Sheet1
from_bus | to_bus | R_OHM | X_OHM | Re_Node_voltages | Imz_Node_voltages | realLoad | reactiveLoad | Re_line_current | Imz_line_current | Re_Node_voltages_iteration_1 | Imz_Node_voltages_iteration_1 | Re_line_current_iteration_1 | Imz_line_current_iteration_1 | Re_Node_voltages_iteration_2 | Imz_Node_voltages_iteration_2 | Err_1_2
substaion UNBVN | branch1 | 0.0922 | 0.0477 | 11.5 | 0 |  |  | 317.8261 | -198.2609 | 11461.2394 | 3.1193 | 334.2259 | -210.0185 | 11459.1665 | 3.4211 | 2.0947
branch1 | branch2 | 0.493 | 0.2511 | 11.5 | 0 | 460 | 220 | 277.8261 | -179.1304 | 11279.2915 | 21.6685 | 293.4058 | -190.5921 | 11266.6597 | 23.7088 | 12.7955
branch2 | H4 | 0.366 | 0.1864 | 11.5 | 0 | 1020 | 490 | 189.1304 | -136.5217 | 11184.6221 | 36.3816 | 202.0676 | -147.0791 | 11165.2874 | 39.8744 | 19.6476
H4 | H5 | 0.3811 | 0.1941 | 11.5 | 0 | 120 | 80 | 178.6957 | -129.5652 | 11091.3726 | 51.074 | 191.2154 | -139.9162 | 11065.2575 | 56.0815 | 26.5908
H5 | branch3 | 0.819 | 0.707 | 11.5 | 0 | 60 | 30 | 173.4783 | -126.9565 | 10859.5356 | 32.4023 | 185.6821 | -137.1702 | 10816.2045 | 37.1466 | 43.5901
branch3 | H3 | 0.1872 | 0.6188 | 11.5 | 0 | 980 | 970 | 88.2609 | -42.6087 | 10816.6469 | -14.2372 | 95.1993 | -47.3745 | 10769.0679 | -12.8942 | 47.598
H3 | H2 | 0.1711 | 1.2351 | 11.5 | 0 | 200 | 100 | 70.8696 | -33.913 | 10762.6351 | -95.9657 | 76.7008 | -37.9182 | 10709.1116 | -101.1395 | 53.773
H2 | H1 | 1.03 | 0.74 | 11.5 | 0 | 200 | 100 | 53.4783 | -25.2174 | 10688.8917 | -109.5657 | 58.0876 | -28.3719 | 10628.2862 | -114.9013 | 60.8398
H1 | H11 | 1.04 | 0.74 | 11.5 | 0 | 60 | 20 | 48.2609 | -23.4783 | 10621.3264 | -120.8613 | 52.4607 | -26.4248 | 10554.1727 | -126.2404 | 67.3688
H11 | H8 | 0.1966 | 0.065 | 11.5 | 0 | 60 | 20 | 43.0435 | -21.7391 | 10611.451 | -119.3852 | 46.8284 | -24.4767 | 10543.3752 | -124.4721 | 68.2656
H8 | H7 | 0.3744 | 0.1238 | 11.5 | 0 | 45 | 30 | 39.1304 | -19.1304 | 10594.4323 | -117.0671 | 42.6127 | -21.5984 | 10524.7472 | -121.6611 | 69.8364
H7 | H9 | 1.468 | 1.155 | 11.5 | 0 | 60 | 35 | 33.913 | -16.087 | 10526.0675 | -132.621 | 36.9553 | -18.2021 | 10449.4733 | -137.6239 | 76.7574
H9 | H10 | 0.5416 | 0.7129 | 11.5 | 0 | 60 | 35 | 28.6957 | -13.0435 | 10501.2272 | -146.0138 | 31.2892 | -14.7904 | 10421.9831 | -151.9195 | 79.4639
H10 | K. Chawla Hostel | 0.591 | 0.526 | 11.5 | 0 | 120 | 80 | 18.2609 | -6.087 | 10487.2333 | -152.0217 | 19.9596 | -6.9978 | 10406.5061 | -158.2825 | 80.9696
K. Chawla Hostel | Alaknanda Bhawan | 0.7463 | 0.545 | 11.5 | 0 | 60 | 10 | 13.0435 | -5.2174 | 10474.6555 | -155.2366 | 14.2469 | -5.9585 | 10392.6262 | -161.6003 | 82.2757
Alaknanda Bhawan | Bhagirathi Bhawan | 1.289 | 1.721 | 11.5 | 0 | 60 | 20 | 5.2174 | -1.7391 | 10464.9372 | -161.974 | 5.7025 | -1.9994 | 10381.8348 | -168.8371 | 83.3854
Bhagirathi Bhawan | Residential Area-1 | 0.732 | 0.574 | 11.5 | 0 | 60 | 20 | 7.8261 | -3.4783 | 10457.212 | -163.9201 | 8.5444 | -3.959 | 10373.3077 | -170.8435 | 84.1894